## UF feed
Laboratoire de la station de dessalement wave 2 EST Jorf Lasfar
Point d'echantillange DEM1-? | [8 empty] | uf feed
Objet : Prestation d’analyse de laboratoire de la station de dessalement d’eau de mer à jorf lasfar
| T (°C) |  |  | pH |  |  | Cond. (mS/cm) à 25° C |  |  | Turb (NTU) |  |  | Cl2 libre (mg/l) |  |  | orp (mv) |  |  | PO43- (mg/l) | MES (mg/l) | TOC (mg/l) | ATP (pg ATP/ml) | Chlorophylle A (µg/l) | SO42- (mg/l) | Al 3+ (mg/l) | NO3 (mg/l) | B (mg/l) | Cl- (mg/l) | TDS (mg/l) | Fe2+ (mg/l) | Fe3+ (mg/l) | Mg2+ (mg/l) | Ca2+ (mg/l) | CO32- (mg/l) | HCO3- (mg/l) | Na (g/l) | SiO2 (mg/l) | HC (mg/l) | Mn (mg/l) | Microbiology (fecal coli) | Microbiology (total coliform) | Microbiology (E-coli)
2025-04-01 | 17.7 | 20 | 18.22 | 8.39 | 8.42 | 8.47 | 50100 | 50700 | 49700 | 6.79 | 4.82 | 4.3 | 0 | 0 | 0 | 176.1 | 173.4 | 171.6
2025-04-02 | 17.6 | 18.3 | 17.3 | 8.35 | 8.39 | 8.42 | 50100 | 50200 | 5000 | 3.2 | 3.99 | 4.27 | 0 | 0 | 0 | 177.1 | 174 | 173
2025-04-03 | 20.9 | 19.5 | 19.1 | 8.44 | 8.44 | 8.46 | 50800 | 50700 | 50600 | 6.26 | 11.5 | 9.55 | 0 | 0.29 | 0 | 174.6 | 174.6 | 174.3
2025-04-04 | 18.4 | 19.3 | 18.4 | 8.24 | 8.31 | 8.29 | 50100 | 50200 | 40900 | 6.52 | 8.49 | 13.3 | 0 | 0.25 | 0 | 176 | 172.5 | 173.6
2025-04-05 | 18.4 | 20.2 | 17.9 | 8.28 | 8.39 | 8.41 | 50100 | 49900 | 49800 | 7.09 | 9.13 | 4.35 | 0 | 0.01 | 0 | 173 | 167.7 | 167.9
2025-04-06 | 18 | 21.7 | 18.8 | 8.34 | 8.34 | 8.38 | 49700 | 50700 | 50900 | 4.89 | 4.09 | 3.37 | 0 | 0 | 0 | 169.4 | 169.5 | 176.9
2025-04-07 | 17.7 | 22.1 | 18.5 | 8.35 | 8.37 | 8.4 | 49800 | 51100 | 51300 | 5.49 | 4.29 | 4.26 | 0 | 0 | 0.56 | 167.7 | 166.4 | 166
2025-04-08 | 17.7 | 23.2 | 19.4 | 8.25 | 8.02 | 8.06 | 50100 | 49800 | 49900 | 3.5 | 4.57 | 4.74 | 0 | 0 | 0.38 | 167.9 | 184.3 | 179.5
2025-04-09 | 18.3 | 20.1 | 19 | 8.1 | 8.17 | 8.19 | 51000 | 50700 | 50400 | 7.59 | 5.42 | 6.92 | 0 | 0 | 0.11 | 179.1 | 175.4 | 171.3
2025-04-10 | 18.1 | 21.3 | 19 | 8.06 | 8.09 | 8.16 | 50900 | 51200 | 49500 | 5.73 | 6.18 | 4.55 | 0.01 | 0 | 0.53 | 179.1 | 170.1 | 172.9
2025-04-11 | 18.3 | 21.3 | 19.4 | 7.96 | 7.92 | 8.07 | 50500 | 50800 | 51000 | 3.31 | 4.22 | 5.1 | 0 | 0 | 0.61 | 183 | 186.4 | 177.5
2025-04-12 | 18.8 | 21.1 | 19.8 | 8.1 | 8.18 | 8.13 | 50700 | 50900 | 50100 | 4.6 | 2.29 | 3.49 | 0 | 0 | 0 | 177.5 | 173.6 | 175.9
2025-04-13 | 19 | 20.3 | 19.8 | 8.15 | 8.12 | 8.22 | 50200 | 50300 | 51100 | 3.39 | 2.18 | 4.94 | 0.53 | 0 | 0.8 | 173.8 | 175.1 | 170.5
2025-04-14 | 18.8 | 21.6 | 19.8 | 8.2 | 8.27 | 8.25 | 50200 | 51100 | 49500 | 2.97 | 2.86 | 3.14 | 0 | 0 | 0 | 171.9 | 167.8 | 165.4
2025-04-15 | 17.7 | 21 | 18.7 | 8.15 | 8.24 | 8.2 | 48900 | 49300 | 50100 | 3.5 | 3.67 | 4.35 | 0 | 0 | 0 | 171.3 | 166.1 | 168.5 | 6.162 | 7.38 | 7.87 | 0.26 | 9.44 | 4010 | <0,005 | <0,05 | 4.056 | 24553 | 30561 | <0,005 | <0,005 | 1480 | 488 | 0 | 146.4 | 11090 | 4.16 | <0,1 | <0,0005 | 110 | 360 | 30
2025-04-16 | 17.8 | 21.4 | 18.3 | 8.21 | 8.29 | 8.27 | 49700 | 50100 | 49100 | 7.76 | 5.08 | 9.03 | 0 | 0 | 0 | 173.8 | 167.9 | 171.3 | 5.13 | 13.52 | 8.68 | 0.22 | 8.89 | 3781 | <0,005 | <0,05 | 4.225 | 25066 | 29951 | <0,005 | <0,005 | 1472 | 510 | 0 | 142.13 | 11131 | 4.28 | <0,1 | <0,0005 | <1 | 160 | 120
2025-04-17 | 16.9 | 21.3 | 19.5 | 8.11 | 7.98 | 7.89 | 49600 | 50300 | 49800 | 4.32 | 4.85 | 4.85 | 0 | 0 | 0 | 173.9 | 178.8 | 186.3 | 5.466 | 10.6 | 11.86 | 0.36 | 9.41 | 3670 | <0,005 | <0,05 | 3.895 | 24150 | 30378 | <0,005 | <0,005 | 1403 | 441 | 0 | 153.11 | 11086 | 4.13 | <0,1 | <0,0005 | <1 | 500 | <1
2025-04-18 | 17.7 | 20.5 | 18.8 | 7.98 | 8.03 | 7.97 | 50100 | 50300 | 49900 | 6.8 | 8.48 | 6.43 | 0 | 0 | 0 | 184.7 | 187.9 | 184.4 | 6.72 | 8.16 | 9.64 | 0.31 | 7.6 | 3192 | <0,005 | <0,05 | 4.513 | 25852 | 30439 | <0,005 | <0,005 | 1419 | 457 | 0 | 145.18 | 12554 | 3.95 | <0,1 | <0,0005 | <1 | 180 | <1
2025-04-19 | 17.8 | 20.3 | 17.7 | 7.97 | 8 | 8.02 | 50000 | 49700 | 50800 | 9.58 | 7.65 | 7.42 | 0.15 | 0 | 0 | 183.5 | 182.2 | 181.2 | 5.424 | 7.32 | 6.77 | 0.37 | 8.06 | 4020 | <0,005 | <0,05 | 3.956 | 24250 | 30988 | <0,005 | <0,005 | 1423 | 431 | 0 | 146.4 | 12461 | 4.24 | <0,1 | <0,0005 | <1 | 210 | 170
2025-04-20 | 16.1 | 19.7 | 17.5 | 8.11 | 8.17 | 8.14 | 49800 | 49900 | 50400 | 10.9 | 9.41 | 10.1 | 0 | 0 | 0 | 177.4 | 173.8 | 175.7 | 5.22 | 12.17 | 8.42 | 0.29 | 9.03 | 3850 | <0,005 | <0,05 | 4.064 | 24987 | 30744 | <0,005 | <0,005 | 1360 | 398 | 0 | 145.18 | 11980 | 4.17 | <0,1 | <0,0005 | <1 | 170 | 130
2025-04-21 | 16.2 | 20.9 | 17.1 | 8.07 | 8.04 | 8.01 | 50400 | 50300 | 49600 | 10.4 | 7.04 | 6.15 | 0 | 0 | 0 | 179.2 | 179.7 | 182.6 | 5.406 | 11.96 | 8.52 | 0.34 | 7.58 | 3913 | <0,005 | <0,05 | 4.319 | 23150 | 30256 | <0,005 | <0,005 | 1398 | 558 | 0 | 147.17 | 11204 | 4.03 | <0,1 | <0,0005 | <1 | 210 | 170
2025-04-22 | 16.5 | 20.9 | 18.4 | 7.84 | 7.94 | 8.04 | 50100 | 50600 | 50700 | 7.45 | 6.19 | 8.38 | 0 | 0 | 0 | 188.6 | 190.9 | 186.7 | 6.66 | 10.54 | 8.71 | 0.29 | 8.12 | 4028 | <0,005 | <0,05 | 4.294 | 22214 | 30927 | <0,005 | <0,005 | 1387 | 560 | 0 | 146.5 | 11263 | 4.012 | <0,1 | <0,0005 | <1 | 200 | 180
2025-04-23 | 16.5 | 20.3 | 18.6 | 8.02 | 8.03 | 8.05 | 51100 | 50200 | 50200 | 8.51 | 7.33 | 6.17 | 0 | 0.64 | 0 | 189.6 | 189.9 | 189.4 | 5.202 | 11.18 | 9.31 | 0.35 | 7.98 | 4101 | <0,005 | <0,05 | 3.982 | 21987 | 30622 | <0,005 | <0,005 | 1425 | 560 | 0 | 146.2 | 12024 | 4.954 | <0,1 | <0,0005 | <1 | 130 | <1
2025-04-24 | 18.3 | 22.5 | 22.5 | 8.02 | 8.09 | 8.04 | 52000 | 51000 | 50700 | 8.2 |  |  | 0 | 0.27 | 0.23 | 190.1 | 186 | 188 | 5.706 | 10 | 8.6 | 0.32 | 7.9 | 4051 | <0,005 | <0,05 | 5.12 | 22319 | 30927 | <0,005 | <0,005 | 1113 | 527 | 0 | 147.3 | 11938 | 4.32 | <0,1 | <0,0005 | <1 | 150 | 90
2025-04-25 | 18.3 | 20.9 | 18.8 | 8.1 | 8.13 | 8.21 | 51300 | 51900 | 50800 | 5.2 |  |  | 0 | 0 | 0 | 183.2 | 181.2 | 178.4 | 6.573 | 8 | 7.81 | 0.34 | 8.19 | 4120 | <0,005 | <0,05 | 4.11 | 21892 | 30988 | <0,005 | <0,005 | 1420 | 562 | 0 | 146.5 | 11250 | 4.29 | <0,1 | <0,0005 | 21 | 39 | 17
2025-04-26 | 18.3 | 20.8 | 18 | 8.05 | 8.07 | 8.05 | 51100 | 50800 | 51700 | 8.85 |  |  | 0 | 0 | 0 | 177.3 | 176.7 | 177.4 | 6.623 | 11.6 | 8.13 | 0.31 | 7.93 | 4112 | <0,005 | <0,05 | 4.19 | 22019 | 31537 | <0,005 | <0,005 | 1385 | 395 | 0 | 146.3 | 11195 | 4.82 | <0,1 | <0,0005 | <1 | 140 | <1
2025-04-27 | 17.4 | 19.7 | - | 8.27 | 8.31 | - | 51500 | 50800 | - | 13.8 |  |  | 0 | 0.19 | - | 171.3 | 173.8 | - | 6.867 | 12.2 | 8.3 | 0.28 | 7.9 | 4090 | <0,005 | <0,05 | 3.961 | 22102 | 30500 | <0,005 | <0,005 | 1427 | 553 | 0 | 147.1 | 11282 | 4.71 | <0,1 | <0,0005 | <1 | 90 | <1
2025-04-28 | 17.5 | 19.8 | - | 8.13 | 8.17 | - | 49700 | 50000 | - | 6.77 |  |  | 0 | 0 | - | 183 | 180.5 | - | 5.26 | 7.61 | 7.83 | 0.36 | 8.17 | 4181 | <0,005 | <0,05 | 4.301 | 23782 | 30317 | <0,005 | <0,005 | - | - | 0 | 146.8 | 10952 | 3.96 | <0,1 | <0,0005 | <1 | 60 | 10
2025-04-29 | 17.6 | 19.8 | 18.2 | 8.33 | 8.34 | 8.36 | 50300 | - | - | 3.41 |  |  | 0 | 0 | 0 | 170.3 | 169.4 | 171.1 | 5.48 | 6.5 | 8.18 | 0.33 | 8.02 | 4219 | <0,005 | <0,05 | 4.321 | 23652 | 30683 | <0,005 | <0,005 | - | - | 0 | 151.17 | 11039 | 4.12 | <0,1 | <0,0005 | <1 | 40 | 15
2025-04-30 | 17.3 | 20.1 | 18.2 | 8.43 | 8.43 | 8.49 | 50900 | - | - | 3.12 |  |  | 0 | 0 | 0.12 | 169.8 | 166.1 | 163.8 | 5.11 | 6.64 | 8.01 | 0.36 | 7.85 | 4160 | <0,005 | <0,05 | 4.29 | 22862 | 31049 | <0,005 | <0,005 | - | - | 0 | 150 | 10958 | 4.31 | <0,1 | <0,0005 | <1 | 190 | <1
2025-05-01 | 16.9 | 20.7 | 19.2 | 8.33 | 8.28 | 8 | 51600 | - | - | 4.43 |  |  | 0 | 0 | 0 | 172.2 | 173.8 | 167 | 5.92 | 8.16 | 8.41 | 0.3 | 7.88 | 4120 | <0,005 | <0,05 | 5.202 | 22670 | 31476 | <0,005 | <0,005 | - | - | 0 | 147.65 | 102321 | 4.22 | <0,1 | <0,0005 | <1 | 180 | <1
2025-05-02 | 18.6 | 22 | 19.3 | 8.48 | 8.44 | 8.46 | 50700 | - | - | 3.25 |  |  | 0 | 0 | 1.05 | 166.9 | 165.8 | 165.9 | 5.7 | 7.49 | 7.92 | 0.32 | 7.93 | 4100 | <0,005 | <0,05 | 5.698 | 22591 | 30927 | <0,005 | <0,005 | - | - | 0 | 147.4 | 9064 | 4.3 | <0,1 | <0,0005 | <1 | 210 | <1
2025-05-03 | 17.7 | 28.2 | 20.1 | 8.44 | 8.3 | 8.43 | 50400 | - | - | 5.76 |  |  | 0 | 0 | 0.92 | 169.1 | 167.1 | 164.5
2025-05-04 | 19.2 | 22.1 | 19.2 | 8.36 | 8.39 | 8.46 | 50600 | - | - | 4.19 |  |  | 0 | 0 | 1.07 | 168.6 | 166.3 | 163.9
2025-05-05 | 17.6 | 22.1 | 19.5 | 8.2 | 8.36 | 8.41 | 51300 | - | - | 5.24 |  |  | 0 | 0 | 0 | 176.4 | 168 | 166.1
2025-05-06 | 17?é |  |  | 8.23 |  |  | 49900 | - | - | 2.8 |  |  | 0 |  |  | 172.1
2025-05-07 | [7 empty] | - | -
2025-05-08 | [7 empty] | - | -
2025-05-09 | [7 empty] | - | -
2025-05-10 | [7 empty] | - | -
2025-05-11 | [7 empty] | - | -
2025-05-12 | [7 empty] | - | -
2025-05-13 | [7 empty] | - | -
2025-05-14 | [7 empty] | - | -
2025-05-15 | [7 empty] | - | -
Nbr analysis | 103 |  |  | 104 |  |  | 90 |  |  | 82 |  |  | 104 |  |  | 104 |  |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18

## PERMEAT UF
Laboratoire de la station de dessalement Jorf Lasfar
PERMEAT ULTRA FILTRATION
Objet : Prestation d’analyse de laboratoire de la station de dessalement d’eau de mer à jorf lasfar
| Cl2 libre (mg/l) |  |  | Turb (NTU) |  |  | PH |  |  | orp (mv)
| P1 | P2 | P3 | P1 | P2 | P3 | P1 | P2 | P3 | P1 | P2 | P3
2025-04-01 | Cl2 libre (mg/l) P1: 0; Cl2 libre (mg/l) P2: 0; Cl2 libre (mg/l) P3: 0.01; Turb (NTU) P1: 0.58; Turb (NTU) P2: 0.64; Turb (NTU) P3: 0.59
2025-04-02 | Cl2 libre (mg/l) P1: 0; Cl2 libre (mg/l) P2: 0; Cl2 libre (mg/l) P3: 0; Turb (NTU) P1: 0.42; Turb (NTU) P2: 0.59; Turb (NTU) P3: 0.56
2025-04-03 | Cl2 libre (mg/l) P1: 0; Cl2 libre (mg/l) P2: 0.03; Cl2 libre (mg/l) P3: 0; Turb (NTU) P1: 0.84; Turb (NTU) P2: 0.44; Turb (NTU) P3: 0.48
2025-04-04 | Cl2 libre (mg/l) P1: 0; Cl2 libre (mg/l) P2: 0.3; Cl2 libre (mg/l) P3: 0; Turb (NTU) P1: 0.66; Turb (NTU) P2: 0.81; Turb (NTU) P3: 0.74
2025-04-05 | Cl2 libre (mg/l) P1: 0; Cl2 libre (mg/l) P2: 0; Cl2 libre (mg/l) P3: O; Turb (NTU) P1: 0.59; Turb (NTU) P2: 0.56; Turb (NTU) P3: 0.54
2025-04-06 | Cl2 libre (mg/l) P1: 0; Cl2 libre (mg/l) P2: 0; Cl2 libre (mg/l) P3: 0; Turb (NTU) P1: 0.57; Turb (NTU) P2: 0.68; Turb (NTU) P3: 0.52
2025-04-07 | Cl2 libre (mg/l) P1: 0; Cl2 libre (mg/l) P2: 0; Cl2 libre (mg/l) P3: 0.53; Turb (NTU) P1: 0.62; Turb (NTU) P2: 0.76; Turb (NTU) P3: 0.79
2025-04-08 | Cl2 libre (mg/l) P1: 0; Cl2 libre (mg/l) P2: 0; Cl2 libre (mg/l) P3: 0.22; Turb (NTU) P1: 0.73; Turb (NTU) P2: 0.69; Turb (NTU) P3: 0.62
2025-04-09 | Cl2 libre (mg/l) P1: 0; Cl2 libre (mg/l) P2: 0; Cl2 libre (mg/l) P3: 0.23; Turb (NTU) P1: 0.64; Turb (NTU) P2: 0.66; Turb (NTU) P3: 0.65
2025-04-10 | Cl2 libre (mg/l) P1: 0; Cl2 libre (mg/l) P2: 0; Cl2 libre (mg/l) P3: 0.3; Turb (NTU) P1: 0.74; Turb (NTU) P2: 0.66; Turb (NTU) P3: 0.62
2025-04-11 | Cl2 libre (mg/l) P1: 0; Cl2 libre (mg/l) P2: 0; Cl2 libre (mg/l) P3: 0; Turb (NTU) P1: 0.63; Turb (NTU) P2: 0.67; Turb (NTU) P3: 0.69
2025-04-12 | Cl2 libre (mg/l) P1: 0; Cl2 libre (mg/l) P2: 0.03; Cl2 libre (mg/l) P3: 0; Turb (NTU) P1: 0.55; Turb (NTU) P2: 0.54; Turb (NTU) P3: 0.65
2025-04-13 | Cl2 libre (mg/l) P1: 0.52; Cl2 libre (mg/l) P2: 0; Cl2 libre (mg/l) P3: 0.55; Turb (NTU) P1: 0.42; Turb (NTU) P2: 0.68; Turb (NTU) P3: 0.55
2025-04-14 | Cl2 libre (mg/l) P1: 0; Cl2 libre (mg/l) P2: 0; Cl2 libre (mg/l) P3: 0; Turb (NTU) P1: 0.52; Turb (NTU) P2: 0.45; Turb (NTU) P3: 0.6
2025-04-15 | Cl2 libre (mg/l) P1: 0; Cl2 libre (mg/l) P2: 0; Cl2 libre (mg/l) P3: 0; Turb (NTU) P1: 0.7; Turb (NTU) P2: 0.52; Turb (NTU) P3: 0.48
2025-04-16 | Cl2 libre (mg/l) P1: 0; Cl2 libre (mg/l) P2: 0; Cl2 libre (mg/l) P3: 0; Turb (NTU) P1: 0.42; Turb (NTU) P2: 0.52; Turb (NTU) P3: 0.62
2025-04-17 | Cl2 libre (mg/l) P1: 0; Cl2 libre (mg/l) P2: 0; Cl2 libre (mg/l) P3: 0; Turb (NTU) P1: 0.42; Turb (NTU) P2: 0.44; Turb (NTU) P3: 0.39
2025-04-18 | Cl2 libre (mg/l) P1: 0; Cl2 libre (mg/l) P2: 0; Cl2 libre (mg/l) P3: 0; Turb (NTU) P1: 0.44; Turb (NTU) P2: 0.42; Turb (NTU) P3: 0.59
2025-04-19 | Cl2 libre (mg/l) P1: 0.05; Cl2 libre (mg/l) P2: 0; Cl2 libre (mg/l) P3: 0; Turb (NTU) P1: 0.35; Turb (NTU) P2: 0.71; Turb (NTU) P3: 0.52
2025-04-20 | Cl2 libre (mg/l) P1: 0; Cl2 libre (mg/l) P2: 0; Cl2 libre (mg/l) P3: 0; Turb (NTU) P1: 0.68; Turb (NTU) P2: 0.52; Turb (NTU) P3: 0.62
2025-04-21 | Cl2 libre (mg/l) P1: 0; Cl2 libre (mg/l) P2: 0; Cl2 libre (mg/l) P3: 0; Turb (NTU) P1: 0.48; Turb (NTU) P2: 0.57; Turb (NTU) P3: 0.62
2025-04-22 | Cl2 libre (mg/l) P1: 0; Cl2 libre (mg/l) P2: 0; Cl2 libre (mg/l) P3: 0; Turb (NTU) P1: 0.59; Turb (NTU) P2: 0.55; Turb (NTU) P3: 0.51
2025-04-23 | Cl2 libre (mg/l) P1: 0; Cl2 libre (mg/l) P2: 0.48; Cl2 libre (mg/l) P3: 0; Turb (NTU) P1: 0.68; Turb (NTU) P2: 0.71; Turb (NTU) P3: 0.75
2025-04-24 | Cl2 libre (mg/l) P1: 0; Cl2 libre (mg/l) P2: 0.19; Cl2 libre (mg/l) P3: 0.19; Turb (NTU) P1: 0.69; Turb (NTU) P2: -; Turb (NTU) P3: -
2025-04-25 | Cl2 libre (mg/l) P1: 0; Cl2 libre (mg/l) P2: 0; Cl2 libre (mg/l) P3: 0; Turb (NTU) P1: 0.55; Turb (NTU) P2: -; Turb (NTU) P3: -
2025-04-26 | Cl2 libre (mg/l) P1: 0; Cl2 libre (mg/l) P2: 0; Cl2 libre (mg/l) P3: 0; Turb (NTU) P1: 0.4; Turb (NTU) P2: -; Turb (NTU) P3: -
2025-04-27 | Cl2 libre (mg/l) P1: 0; Cl2 libre (mg/l) P2: 0; Cl2 libre (mg/l) P3: -; Turb (NTU) P1: 0.55; Turb (NTU) P2: 0.61; Turb (NTU) P3: -
2025-04-28 | Cl2 libre (mg/l) P1: 0; Cl2 libre (mg/l) P2: 0; Cl2 libre (mg/l) P3: -; Turb (NTU) P1: 0.45; Turb (NTU) P2: 0.52; Turb (NTU) P3: -
2025-04-29 | 0 | 0 | 0 | 0.54 | 0.79 | - |  | 8.29 | 8.27 |  | 171.5 | 171.5
2025-04-30 | 0 | 0 | 0 | 0.46 | 0.41 | - | 8.44 | 8.43 | 8.41 | 168.9 | 166.3 | 167.1
2025-05-01 | 0 | 0 | 0 | 0.5 | 0.58 | - | 8.28 | 8.21 | 8.36 | 174.5 | 176.8 | 170.2
2025-05-02 | 0 | 0 | 0.6 | 0.68 | 0.65 | - | 8.29 | 8.45 | 8.45 | 172.4 | 165.6 | 166.8
2025-05-03 | 0 | 0 | 0.85 | 0.73 | 0.75 |  | 8.41 | 8.29 | 8.38 | 172.4 | 165.1 | 173.5
2025-05-04 | 0 | 0 | 0.88 | 0.71 | 0.67 |  | 8.32 | 8.34 | 8.47 | 170.5 | 172.4 | 163.4
2025-05-05 | 0 | 0 | 0 | 0.63 | 0.68 |  | 8.09 | 8.31 | 8.4 | 184 | 170.4 | 166.7
2025-05-06 | Cl2 libre (mg/l) P1: 0; Turb (NTU) P1: 0.56; PH P1: 8.21; orp (mv) P1: 173.2
2025-05-07
2025-05-08
2025-05-09
2025-05-10
2025-05-11
2025-05-12
2025-05-13
2025-05-14
2025-05-15
Nbr analysis | Cl2 libre (mg/l) P1: 103; Turb (NTU) P1: 91; PH P1: 21; orp (mv) P1: 21

## AVANT FC sud
Laboratoire de la station de dessalement Jorf Lasfar
AVANT FILTRES A CARTOUCHES
Objet : Prestation d’analyse de laboratoire de la station de dessalement d’eau de mer à jorf lasfar
SDI
| P1 | P2 | P3
2024-04-01 | 2.53 | 2.62 | 2.32
2024-04-02 | 2.28 | 2.36 | 2.67
2024-04-03 | 2.59 | 3.26 | 3.16
2024-04-04 | 2.86 | 2.8 | 2.53
2024-04-05 | 2.86 | 3.19 | 2.96
2024-04-06 | 2.97 | 2.73 | 3.5
2024-04-07 | 2.9 | 3.02 | 3.07
2024-04-08 | 2.92 | 3.11 | 3.25
2024-04-09 | 3.2 | 3.15 | 3.15
2024-04-10 | 3.01 | 2.95 | 3.04
2024-04-11 | 2.64 | 3 | 2.96
2024-04-12 | 2.83 | 2.92 | 3.05
2024-04-13 | 2.73 | 2.8 | 2.67
2024-04-14 | 2.74 | 2.65 | 2.67
2024-04-15 | 2.72 | 3.27 | 3.15
2024-04-16 | 3.2 | 2.96 | 2.87
2024-04-17 | 2.91 | 2.76 | 2.86
2024-04-18 | 2.88 | 2.98 | 2.86
2024-04-19 | 2.55 | 2.74 | 2.8
2024-04-20 | 2.87 | 2.77 | 2.85
2024-04-21 | 2.73 | 2.7 | 2.87
2024-04-22 | 2.92 | 2.86 | 2.72
2024-04-23 | 2.9 | 3.43 | 2.65
2024-04-24 | 2.61 | - | -
2024-04-25 | 3.01 | - | -
2024-04-26 | 2.96 | - | -
2024-04-27 | 2.85 | - | -
2024-04-28 | 2.91 | - | -
2024-04-29 | 3.04 | - | -
2024-04-30 | 2.62 | - | -
2024-05-01 | 2.7 | - | -
2024-05-02 | 3.84 | - | -
2024-05-03 | 3.17 | - | -
2024-05-04 | 3.07 | - | -
2024-05-05 | 2.83 | - | -
2024-05-06 | 3.12 | - | -
2024-05-07 |  | - | -
2024-05-08 |  | - | -
2024-05-09 |  | - | -
2024-05-10 |  | - | -
2024-05-11 |  | - | -
2024-05-12 |  | - | -
2024-05-13 |  | - | -
2024-05-14 |  | - | -
2024-05-15 |  | - | -
Nbr analysis | 82

## AVANT FC nord
Laboratoire de la station de dessalement Jorf Lasfar
AVANT FILTRES A CARTOUCHES
Objet : Prestation d’analyse de laboratoire de la station de dessalement d’eau de mer à jorf lasfar
SDI15
| P1 | P2 | P3
2025-04-01 | 2.67 | 2.71 | 2.57
2025-04-02 | 2.41 | 2.54 | 2.93
2025-04-03 | 2.87 | 2.82 | 2.78
2025-04-04 | 2.57 | 3.1 | 2.72
2025-04-05 | 2.66 | 3.06 | 2.81
2025-04-06 | 2.9 | 2.85 | 2.98
2025-04-07 | 3.01 | 2.94 | 2.9
2025-04-08 | 2.78 | 3.2 | 3.09
2025-04-09 | 3.07 | 3.24 | 3.19
2025-04-10 | 3.26 | 3.18 | 3.17
2025-04-11 | 3.6 | 3.07 | 3.14
2025-04-12 | 3.04 | 3.18 | 3.19
2025-04-13 | 3.05 | 3.15 | 2.96
2025-04-14 | 2.89 | 3.09 | 2.96
2025-04-15 | 3.02 | 2.92 | 2.89
2025-04-16 | 2.95 | 3.1 | 3.19
2025-04-17 | 3.1 | 3.2 | 3.07
2025-04-18 | 3.23 | 3.29 | 3.15
2025-04-19 | 2.68 | 3.05 | 3.1
2025-04-20 | 3.09 | 2.94 | 3.17
2025-04-21 | 3.02 | 3.06 | 3.14
2025-04-22 | 3.17 | 3.12 | 3.04
2025-04-23 | 3.2 | 2.2 | 2.53
2025-04-24 | 2.43 | - | -
2025-04-25 | 2.64 | - | -
2025-04-26 | 2.7 | - | -
2025-04-27 | 2.77 | - | -
2025-04-28 | 2.82 | - | -
2025-04-29 | 2.79 | - | -
2025-04-30 | 2.8 | - | -
2025-05-01 | 2.96 | - | -
2025-05-02 | 2.48 | - | -
2025-05-03 | 3.46 | - | -
2025-05-04 | 3.56 | - | -
2025-05-05 | 3.1 | - | -
2025-05-06 | 3.9 | - | -
2025-05-07 |  | - | -
2025-05-08 |  | - | -
2025-05-09 |  | - | -
2025-05-10 |  | - | -
2025-05-11 |  | - | -
2025-05-12 |  | - | -
2025-05-13 |  | - | -
2025-05-14 |  | - | -
2025-05-15 |  | - | -
Nbr analysis | 82

## cf outlet
Laboratoire de la station de dessalement Jorf Lasfar
APRES FILTRES A CARTOUCHES
Objet : Prestation d’analyse de laboratoire de la station de dessalement d’eau de mer à jorf lasfar
[7 empty] | nord | [18 empty] | sud
| T (°C) |  |  | Cond. (mS/cm) à 25° C |  |  | pH |  |  | Turb (NTU) |  |  | Cl2 libre (mg/l) |  |  | orp (mv) n |  |  | T (°C) s |  |  | Cond. (mS/cm) à 25° C s |  |  | pH |  |  | Turb (NTU) s |  |  | Cl2 libre (mg/l) s |  |  | orp (mv) s |  |  | PO43- (mg/l) | Fe3+ (mg/l) | Fe3+ (mg/l) | TDS (mg/l) | TSS (mg/l) | Microbiology (fecal coli) | Microbiology (total coliform) | Microbiology (E-coli) | ATP (pg ATP/ml) | O&G (mg/l) | Mn (mg/l) | TOC (mg/l) | Chloropyll (µg/l)
2025-04-01 | 17.6 | 20.2 | 18.3 | 49200 | 49400 | 48600 | 8.36 | 8.38 | 8.46 | 0.44 | 0.51 | 0.47 | 0 | 0 | 0.01 | 177.4 | 175.1 | 172.2 | 17.7 | 20.1 | 18.1 | 48700 | 48900 | 48200 | 1900-01-07 09:07 | 8.35 | 8.43 | 0.52 | 0.59 | 0.41 | 0 | 0 | 0.01 | 176.7 | 176.5 | 173.5
2025-04-02 | 17.8 | 18.3 | 17.1 | 49300 | 49700 | 48800 | 8.32 | 8.36 | 8.27 | 0.25 | 0.51 | 0.44 | 0 | 0 | 0 | 178.5 | 175.2 | 179.3 | 17.7 | 18.4 | 17 | 48900 | 49400 | 49300 | 8.35 | 8.32 | 8.39 | 0.3 | 0.46 | 1.62 | 0 | 0 | 0 | 179.5 | 177.2 | 173.9
2025-04-03 | 20.8 | 19.3 | 19 | 49000 | 48900 | 49000 | 8.31 | 8.41 | 8.48 | 0.36 | 0.45 | 0.3 | 0 | 0 | 0 | 174.6 | 174.2 | 172.9 | 20.9 | 19.2 | 18.9 | 49600 | 49100 | 49200 | 8.39 | 8.35 | 8.5 | 0.73 | 0.52 | 0.62 | 0 | 0 | 0 | 176.9 | 178.5 | 172.3
2025-04-04 | 18.5 | 19.7 | 18.4 | 48600 | 48500 | 48000 | 8.22 | 8.14 | 8.22 | 0.45 | 0.69 | 0.57 | 0 | 0 | 0 | 177.3 | 180.4 | 177.2 | 18.6 | 19.7 | 18.4 | 48900 | 48700 | 4800 | 8.2 | 8.26 | 8.14 | 0.51 | 0.5 | 0.53 | 0 | 0 | 0 | 178.2 | 174.8 | 180.8
2025-04-05 | 18.5 | 19.6 | 18.3 | 48400 | 48300 | 48400 | 8.25 | 8.27 | 8.4 | 0.37 | 0.45 | 0.27 | 0 | 0 | 0 | 174.7 | 173 | 168 | 18.6 | 19.8 | 17.9 | 48700 | 48600 | 48700 | 8.18 | 8.35 | 8.39 | 0.48 | 0.59 | 0.3 | 0 | 0 | 0 | 177.6 | 169.6 | 168.1
2025-04-06 | 18 | 22 | 18.7 | 47300 | 49600 | 49800 | 8.3 | 8.33 | 8.32 | 0.65 | 0.42 | 0.46 | 0 | 0 | 0 | 171.3 | 169.9 | 170.9 | 18 | 22.1 | 19 | 47700 | 49900 | 50000 | 8.33 | 8.3 | 8.27 | 0.43 | 0.35 | 0.48 | 0 | 0 | 0 | 169.9 | 171.1 | 173.3
2025-04-07 | 17.1 | 22.2 | 18.7 | 47900 | 49700 | 5000 | 8.25 | 8.36 | 8.28 | 0.42 | 0.35 | 0.35 | 0 | 0 | 0.12 | 172 | 167.1 | 171.5 | 17.2 | 22.2 | 18.5 | 48100 | 49900 | 49900 | 8.33 | 8.34 | 8.37 | 0.51 | 0.42 | 0.52 | 0 | 0 | 0 | 168.8 | 168 | 167.2
2025-04-08 | 17.8 | 25.6 | 19.5 | 48700 | 47500 | 48700 | 8.2 | 8.08 | 8.01 | 0.46 | 0.52 | 0.46 | 0 | 0 | 0 | 178.3 | 181 | 181.5 | 17.7 | 25.8 | 19.5 | 48400 | 47800 | 49200 | 8.18 | 8.1 | 8 | 0.59 | 0.47 | 0.58 | 0 | 0 | 0 | 168.2 | 180.2 | 182.3
2025-04-09 | 18.2 | 20.6 | 19 | 49400 | 48100 | 48300 | 8.07 | 8.14 | 8.15 | 0.48 | 0.43 | 0.49 | 0 | 0 | 0 | 180.7 | 176.5 | 173.1 | 18.1 | 20.5 | 19.1 | 49700 | 48800 | 48500 | 7.99 | 8.1 | 8.11 | 0.59 | 0.51 | 0.55 | 0 | 0 | 0 | 184.3 | 178.5 | 175.1
2025-04-10 | 18 | 20.7 | 19 | 48600 | 49700 | 48500 | 7.91 | 7.97 | 8.15 | 0.35 | 0.5 | 0.53 | 0 | 0 | 0 | 179 | 182.2 | 174.1 | 17.9 | 20.9 | 19.1 | 48800 | 50300 | 47500 | 8.01 | 8.02 | 8.16 | 0.28 | 0.37 | 0.49 | 0 | 0 | 0 | 181.7 | 180.9 | 165.4
2025-04-11 | 18.2 | 21.4 | 19.4 | 48300 | 48600 | 47900 | 7.85 | 7.8 | 8.08 | 0.51 | 0.63 | 0.61 | 0 | 0 | 0 | 188.9 | 187.7 | 176.8 | 18.1 | 21.1 | 19.2 | 48600 | 49200 | 48100 | 7.88 | 7.83 | 8.02 | 0.49 | 0.48 | 0.55 | 0 | 0 | 0 | 186.9 | 185.1 | 179.3
2025-04-12 | 18.9 | 20.8 | 20 | 49300 | 49100 | 49400 | 8.06 | 8.09 | 8.11 | 0.44 | 0.44 | 0.49 | 0 | 0 | 0 | 179.2 | 177.5 | 176.3 | 18.8 | 22.4 | 19.9 | 49500 | 49400 | 49200 | 8.03 | 8.15 | 8.1 | 0.39 | 0.5 | 0.53 | 0 | 0 | 0 | 180.9 | 174.3 | 178.1
2025-04-13 | 19.2 | 20.2 | 19.9 | 49600 | 49500 | 48300 | 8.1 | 8.1 | 8.15 | 0.39 | 0.47 | 0.43 | 0.22 | 0 | 0.31 | 175.8 | 175.9 | 173.5 | 18.9 | 20.2 | 19.7 | 49300 | 49200 | 48700 | 8.08 | 8.1 | 8.17 | 0.27 | 0.66 | 0.49 | 0 | 0 | 0 | 176.9 | 175.6 | 172.3
2025-04-14 | 18.6 | 21.7 | 19.5 | 48300 | 49100 | 48500 | 8.19 | 8.24 | 8.28 | 0.45 | 0.42 | 0.55 | 0 | 0 | 0 | 172.1 | 169.7 | 168 | 18.7 | 21.9 | 19.4 | 48700 | 49400 | 48900 | 8.17 | 8.2 | 8.17 | 0.42 | 0.36 | 0.39 | 0 | 0 | 0 | 173.4 | 171 | 172.8
2025-04-15 | 17.8 | 21.1 | 19 | 47100 | 48100 | 47100 | 8.2 | 8.22 | 8.24 | 0.38 | 0.27 | 0.29 | 0 | 0 | 0 | 168.3 | 167 | 166.5 | 17.8 | 21.2 | 18.6 | 46900 | 47700 | 46900 | 8.18 | 8.19 | 8.21 | 0.4 | 0.45 | 0.35 | 0 | 0 | 0 | 169.8 | 168.7 | 167.9 | 6.042 | <0,005 | <0,005 | 29585 | 4.22 | <1 | 150 | 200 | 0.22 | <0,1 | <0,005 | 4.61 | 3.16
2025-04-16 | 17.6 | 21.6 | 18.5 | 48700 | 49100 | 48700 | 8.13 | 8.22 | 8.18 | 0.4 | 0.44 | 0.4 | 0 | 0 | 0 | 176.5 | 170.7 | 169.5 | 17.7 | 21.8 | 18.6 | 48200 | 48800 | 48300 | 8.15 | 8.25 | 8.22 | 0.37 | 0.28 | 0.42 | 0 | 0 | 0 | 170.2 | 170.2 | 169.5 | 5.04 | <0,005 | <0,005 | 28731 | 5.63 | <1 | <1 | <1 | 0.17 | <0,1 | <0,005 | 5.47 | <2
2025-04-17 | 16.4 | 21 | 19.5 | 48100 | 47500 | 48200 | 8.16 | 7.9 | 7.91 | 0.28 | 0.36 | 0.25 | 0 | 0 | 0 | 170.7 | 180.7 | 185.2 | 16.8 | 21.1 | 19.6 | 47900 | 46800 | 47900 | 8.11 | 7.92 | 7.92 | 0.34 | 0.38 | 0.32 | 0 | 0 | 0 | 170.1 | 181.7 | 184.5 | 5.4 | <0,005 | <0,005 | 29707 | 4.52 | <1 | 160 | 150 | 0.31 | <0,1 | <0,005 | 8.61 | 3.1
2025-04-18 | 17.2 | 20.6 | 18.6 | 48400 | 49100 | 46500 | 7.87 | 7.89 | 7.91 | 0.26 | 0.27 | 0.42 | 0 | 0 | 0 | 190.3 | 190.6 | 186.4 | 17.6 | 20.6 | 18.7 | 48100 | 49200 | 47500 | 7.9 | 7.91 | 7.89 | 0.45 | 0.35 | 0.37 | 0 | 0 | 0 | 188.8 | 190.1 | 187.4 | 6.6 | <0,005 | <0,005 | 29402 | 4.11 | <1 | 140 | <1 | 0.27 | <0,1 | <0,005 | 6.15 | <2
2025-04-19 | 17.6 | 20.5 | 17.8 | 47200 | 48400 | 47900 | 7.73 | 7.92 | 7.9 | 0.3 | 0.5 | 0.32 | 0 | 0 | 0 | 195 | 185.1 | 186.8 | 17.8 | 21.7 | 18 | 47000 | 48200 | 48400 | 7.92 | 7.89 | 7.94 | 0.28 | 0.43 | 0.4 | 0 | 0 | 0 | 186.1 | 186.8 | 184.9 | 5.28 | <0,005 | <0,005 | 28365 | 3.83 | <1 | 890 | 820 | 0.33 | <0,1 | <0,005 | 4.86 | <2
2025-04-20 | 16.6 | 19.5 | 17.7 | 48200 | 48200 | 47600 | 8.05 | 8.03 | 8.14 | 0.34 | 0.33 | 0.23 | 0 | 0 | 0 | 180 | 179.8 | 175.9 | 16.4 | 19.5 | 17.6 | 47900 | 47800 | 48900 | 8.05 | 8.13 | 8.11 | 0.53 | 0.33 | 0.23 | 0 | 0 | 0 | 180.2 | 175.9 | 177.1 | 4.8 | <0,005 | <0,005 | 29219 | 4.1 | <1 | 100 | <1 | 0.21 | <0,1 | <0,005 | 4.92 | 2.54
2025-04-21 | 16.5 | 21.8 | 17.3 | 47900 | 48200 | 48300 | 8.06 | 7.55 | 7.95 | 0.35 | 0.55 | 0.51 | 0 | 0 | 0 | 179.2 | 202.8 | 184.9 | 16.1 | 20.4 | 17.1 | 49100 | 49200 | 48900 | 8.04 | 7.96 | 7.88 | 0.32 | 0.49 | 0.37 | 0 | 0 | 0 | 180.2 | 183.2 | 188.5 | 5.172 | <0,005 | <0,005 | 29036 | 3.9 | <1 | 180 | 150 | 0.24 | <0,1 | <0,005 | 4.35 | <2
2025-04-22 | 16.3 | 21.3 | 18.2 | 46900 | 48100 | 48200 | 7.73 | 7.8 | 7.79 | 0.34 | 0.39 | 0.49 | 0 | 0 | 0 | 193.7 | 197.7 | 193.8 | 16.2 | 21.7 | 18.3 | 47900 | 48600 | 48600 | 7.69 | 7.86 | 8 | 0.36 | 0.42 | 0.32 | 0 | 0 | 0 | 195.6 | 195 | 188.7 | 6.54 | <0,005 | <0,005 | 29463 | 4 | <1 | 180 | 170 | 0.19 | <0,1 | <0,005 | 4,1_ | 3.22
2025-04-23 | 16.3 | 20.6 | 20.3 | 47400 | 48900 | 48700 | 7.92 | 7.84 | 7.5 | 0.36 | 0.39 | 0.5 | 0 | 0 | 0 | 194.3 | 169.2 | 214.9 | 16.5 | 20.7 | 18.8 | 48000 | 49500 | 48900 | 7.95 | 7.93 | 7.96 | 0.42 | 0.53 | 0.5 | 0 | 0 | 0 | 193.3 | 191.7 | 193.2 | 4.86 | <0,005 | <0,005 | 29402 | 4.22 | <1 | 110 | <1 | 0.28 | <0,1 | <0,005 | 5.17 | 3.19
2025-04-24 | 18.5 | 22.3 | 19.3 | 49200 | 48500 | 48800 | 7.91 | 7.96 | 7.95 | 0.47 | - | - | 0 | 0 | 0.16 | 193.4 | 192.2 | 192.7 | 18.2 | 22 | 19.4 | 49100 | 49700 | 49100 | 7.95 | 7.97 | 7.89 | 0.53 | - | - | 0 | 0.11 | 0 | 192.1 | 191.9 | 191.4 | 5.472 | <0,005 | <0,005 | 29707 | 4.12 | <1 | 90 | 20 | 0.26 | <0,1 | <0,005 | 4.16 | <2
2025-04-25 | 18.3 | 20.4 | 18.5 | 48700 | 48900 | 48400 | 7.99 | 8.02 | 8.15 | 0.42 | - | - | 0 | 0 | 0 | 188.2 | 186.1 | 185.6 | 18.3 | 20.6 | 18.3 | 47900 | 47600 | 48100 | 8.05 | 8.04 | 8.12 | 0.36 | - | - | 0 | 0 | 0 | 185.8 | 185.8 | 182.5 | 6.132 | <0,005 | <0,005 | 27417 | 3.16 | 15 | 180 | 12 | 0.28 | <0,1 | <0,005 | 5.19 | 3.21
2025-04-26 | 18.2 | 20.7 | 18.1 | 49500 | 49100 | 49500 | 8.02 | 8.02 | 8 | 0.35 | - | - | 0 | 0 | 0 | 179 | 179.3 | 180 | 18.4 | 21 | 18.2 | 49200 | 48300 | 48900 | 7.97 | 8 | 8.03 | 0.32 | - | - | 0 | 0 | 0 | 181.3 | 180.7 | 178.5 | 6.377 | <0,005 | <0,005 | 28215 | 3.03 | <1 | 160 | <1 | 0.26 | <0,1 | <0,005 | 4.3 | 2.98
2025-04-27 | 17.2 | 19.4 | - | 49600 | 49000 | - | 8.2 | 8.15 | - | 0.29 | - | - | 0 | 0 | - | 174.7 | 174.1 | - | 17.2 | 19.3 | - | 49100 | 49400 | - | 8.14 | 8.19 | - | 0.41 | - | - | 0 | 0 | - | 177.4 | 175.3 | - | 6.67 | <0,005 | <0,005 | 27930 | 3.23 | <1 | 110 | <1 | 0.22 | <0,1 | <0,005 | 4.29 | 2.94
2025-04-28 | 17.8 | 19.6 | - | 48900 | 48900 | - | 8.09 | 8.09 | - | 0.42 | - | - | 0 | 0.03 | - | 184.4 | 184 | - | 17.7 | 19.4 | - | 48100 | 48200 | - | 8.23 | 8.15 | - | 0.23 | - | - | 0 | 0 | - | 178.1 | 181.8 | - | 7.72 | <0,005 | <0,005 | - | 3.19 | <1 | 70 | <1 | 0.2 | <0,1 | <0,005 | 3.91 | <2
2025-04-29 | 17.7 | 19.2 | 18.2 | 49100 | - | - | 8.28 | 8.32 | 8.21 | 0.24 | - | - | 0 | 0 | 0 | 172.6 | 170.4 | 177.5 | 17.4 | 19.3 | 18.6 | 48700 | - | - | 8.24 | 8.32 | 8.25 | 0.21 | - | - | 0 | 0 | 0 | 174.2 | 170.4 | 175.6 | 6.53 | <0,005 | <0,005 | - | 4.04 | <1 | 60 | 10 | 0.31 | <0,1 | <0,005 | 4.1 | 2.52
2025-04-30 | 17 | 20.1 | 18.1 | - | - | - | 8.36 | 8.41 | 8.47 | 0.36 | - | - | 0 | 0 | 0 | 172.7 | 167.4 | 165 | 17 | 20.2 | 18.2 | 47900 | - | - | 8.42 | 8.38 | 8.48 | 0.4 | - | - | 0 | 0 | 0 | 170.1 | 168.8 | 164.5 | 6.62 | <0,005 | <0,005 | - | 4.22 | <1 | 170 | <1 | 0.27 | <0,1 | <0,005 | 3.9 | 3.04
2025-05-01 | 17.1 | 21 | 18.8 | - | - | - | 8.31 | 8.16 | 8.42 | 0.4 | - | - | 0 | 0 | 0 | 172.8 | 179.4 | 164.3 | 16.9 | 20.8 | 18.8 | - | - | - | 8.24 | 8.13 | 8.4 | 0.33 | - | - | 0 | 0 | 0 | 176.4 | 180.5 | 168 | 5.83 | <0,005 | <0,005 | - | 4.1 | <1 | 200 | <1 | 0.26 | <0,1 | <0,005 | 4.17 | 2.58
2025-05-02 | 18.7 | 22 | 19.5 | - | - | - | 8.35 | 8.36 | 8.43 | 0.49 | - | - | 0 | 0 | 0 | 171.6 | 169.2 | 167.3 | 18.6 | 21.8 | 19.5 | - | - | - | 8.38 | 8.42 | 8.41 | 0.33 | - | - | 0 | 0 | 0 | 173.5 | 166.9 | 168.2 | 5.67 | <0,005 | <0,005 | - | 4.21 | <1 | 160 | <1 | 0.29 | <0,1 | <0,005 | 3.91 | <2
2025-05-03 | 17.5 | 20.8 | 19.5 | - | - | - | 8.38 | 8.35 | 8.29 | 0.51 | - | - | 0 | 0 | 0.19 | 170.4 | 165.7 | 170.5 | 17.2 | 21 | 19.8 | - | - | - | 8.37 | 8.38 | 8.32 | 0.47 | - | - | 0 | 0 | 0 | 168.1 | 166.2 | 173.2
2025-05-04 | 18.7 | 21.8 | 19.1 | - | - | - | 8.35 | 8.3 | 8.29 | 0.33 | - | - | 0 | 0 | 0.44 | 169.5 | 167.4 | 170.7 | 18.7 | 21.9 | 19.1 | - | - | - | 8.3 | 8.27 | 8.41 | 0.3 | - | - | 0 | O | 0.4 | 171.6 | 168.4 | 166.2
2025-05-05 | 18.4 | 21.9 | 19.6 | - | - | - | 8 | 8.33 | 8.38 | 0,,44 | - | - | 0 | 0 | 0 | 180 | 169.6 | 167.4 | 18.3 | 22.2 | 19.5 | - | - | - | 8.02 | 8.3 | 8.35 | 0.35 | - | - | 0 | 0 | 0 | 179 | 170.7 | 168.9
2025-05-06 | 17.5 |  |  | - | - | - | 8.21 |  |  | 0.44 | - | - | 0 |  |  | 173.2 |  |  | 17.6 |  |  | - | - | - | 8.2 |  |  | 0.42 | - | - | à |  |  | 173.8
2025-05-07 |  |  |  | - | - | - |  |  |  |  | - | - | [9 empty] | - | - | - |  |  |  |  | - | -
2025-05-08 |  |  |  | - | - | - |  |  |  |  | - | - | [9 empty] | - | - | - |  |  |  |  | - | -
2025-05-09 |  |  |  | - | - | - |  |  |  |  | - | - | [9 empty] | - | - | - |  |  |  |  | - | -
2025-05-10 |  |  |  | - | - | - |  |  |  |  | - | - | [9 empty] | - | - | - |  |  |  |  | - | -
2025-05-11 |  |  |  | - | - | - |  |  |  |  | - | - | [9 empty] | - | - | - |  |  |  |  | - | -
2025-05-12 |  |  |  | - | - | - |  |  |  |  | - | - | [9 empty] | - | - | - |  |  |  |  | - | -
2025-05-13 |  |  |  | - | - | - |  |  |  |  | - | - | [9 empty] | - | - | - |  |  |  |  | - | -
2025-05-14 |  |  |  | - | - | - |  |  |  |  | - | - | [9 empty] | - | - | - |  |  |  |  | - | -
2025-05-15 |  |  |  | - | - | - |  |  |  |  | - | - | [9 empty] | - | - | - |  |  |  |  | - | -
Nbr analysis | 104 |  |  | 83 |  |  | 104 |  |  | 81 |  |  | 104 |  |  | 104 |  |  | 104 |  |  | 84 |  |  | 104 |  |  | 82 |  |  | 102 |  |  | 104 |  |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18

## PERMEAT RO
Laboratoire de la station de dessalement Jorf Lasfar
PERMEAT RO (OSMOSE INVERSE)
Objet : Prestation d’analyse de laboratoire de la station de dessalement d’eau de mer à jorf lasfar
| COMMUN | [8 empty] | 1ère pass | [55 empty] | TDS(mg/l) | Microbiology (fecal coli) (ufc/100ml) | Microbiology total coliform (ufc/100ml) | Microbiology (E-coli) (ufc/100ml) | Fe2+ (mg/l) | Fe3+ (mg/l) | CO3 (mg/l) | HCO3 (mg/l) | As (mg/l) | Na (mg/l) | Cl (mg/l) | SO4 (mg/l) | NO3 (mg/l) | NO2 (mg/l) | B (mg/l) | Al (mg/l) | Pb (mg/l) | Cd (µg/l) | Cu (mg/l) | CO2 (mg/l)
| Cond. à 25° C |  |  | PH |  |  | orp (mv) |  |  | Train A | [6 empty] | Train B | [6 empty] | Train C | [6 empty] | Train D | [6 empty] | Train E | [6 empty] | Train F | [6 empty] | Train G | [6 empty] | Train H
[10 empty] | Cond à 25° C |  |  | PH |  | orp (mv) |  | Cond à 25° C |  |  | PH |  | orp (mv) |  | Cond à 25° C |  |  | PH |  | orp (mv) |  | Cond à 25° C |  |  | PH |  | orp (mv) |  | Cond à 25° C |  |  | PH |  | orp (mv) |  | Cond à 25° C |  |  | PH |  | orp (mv) |  | Cond à 25° C |  |  | PH |  | orp (mv) |  | Cond à 25° C |  |  | PH |  | orp (mv)
2024-04-01 | 312 | 312 | 316 | 6.25 | 6.09 | 6.36 |  |  |  | - | - | - |  |  |  |  | 487 | 453 | 497 |  |  |  |  | 382 | 382 | 385 |  |  |  |  | 365 | 354 | 346 |  |  |  |  | 173 | 185 | 169 |  |  |  |  | 231 | 235 | 236 |  |  |  |  | 283 | 287 | 293 |  |  |  |  | 319 | 322 | 328
2024-04-02 | 358 | 370 | 339 | 6.33 | 6.14 | 6.55 |  |  |  | - | 504 | 482 |  |  |  |  | 476 | 473 | 435 |  |  |  |  | 384 | 397 | 362 |  |  |  |  | 339 | 351 | 313 |  |  |  |  | - | - | - |  |  |  |  | 245 | 250 | 224 |  |  |  |  | 292 | 303 | 278 |  |  |  |  | 328 | 339 | 312
2024-04-03 | 343 | 310 | 325 | 5.98 | 6.11 | 6.2 |  |  |  | 449 | - | - |  |  |  |  | 426 | 543 | 447 |  |  |  |  | 364 | 376 | 376 |  |  |  |  | 317 | 321 | 322 |  |  |  |  | - | - | - |  |  |  |  | 248 | 236 | 235 |  |  |  |  | 275 | 286 | 294 |  |  |  |  | 330 | 320 | 326
2024-04-04 | 316 | 416 | 317 | 6.15 | 6.27 | 6.32 |  |  |  | - | - | - |  |  |  |  | 437 | 460 | 456 |  |  |  |  | 380 | 388 | 372 |  |  |  |  | 323 | 327 | 340 |  |  |  |  | 188 | 183 | 175 |  |  |  |  | 237 | 240 | 249 |  |  |  |  | 295 | 301 | 318 |  |  |  |  | 328 | 335 | 424
2024-04-05 | 303 | 336 | 2999 | 6.14 | 6.43 | 6.29 |  |  |  | - | - | - |  |  |  |  | 454 | 452 | 446 |  |  |  |  | 367 | 381 | 409 |  |  |  |  | 311 | 324 | 315 |  |  |  |  | 165 | 178 | 174 |  |  |  |  | 229 | 236 | 224 |  |  |  |  | 289 | 303 | 293 |  |  |  |  | 321 | 398 | -
2024-04-06 | 315 | 314 | 320 | 6.38 | 6.17 | 7 |  |  |  | - | - | - |  |  |  |  | 466 | 416 | 435 |  |  |  |  | 354 | 354 | - |  |  |  |  | 297 | 295 | 310 |  |  |  |  | 155 | 153 | 162 |  |  |  |  | - | - | - |  |  |  |  | 280 | 280 | 293 |  |  |  |  | 370 | 366 | 378
2024-04-07 | 447 | 330 | 359 | 6.3 | 6.26 | 6.96 |  |  |  | - | - | - |  |  |  |  | 453 | 440 | 439 |  |  |  |  | 383 | 392 | 384 |  |  |  |  | 294 | 310 | 309 |  |  |  |  | 151 | 165 | 160 |  |  |  |  | - | - | - |  |  |  |  | 288 | 292 | 295 |  |  |  |  | 367 | 395 | 394
2024-04-08 | 334 | 325 | 349 | 6.24 | 6.19 | 6.01 |  |  |  | - | 516 | 484 |  |  |  |  | 307 | 392 | 420 |  |  |  |  | 350 | 355 | 360 |  |  |  |  | - | - | 320 |  |  |  |  | 242 | 150 | 150 |  |  |  |  | - | - | - |  |  |  |  | 273 | 278 | 280 |  |  |  |  | 346 | 350 | 351
2024-04-09 | 395 | 320 | 471 | 6.01 | 6.2 | 6.05 |  |  |  | 460 | 470 | 626 |  |  |  |  | 407 | 406 | 542 |  |  |  |  | - | - | 569 |  |  |  |  | 421 | - | 499 |  |  |  |  | 145 | 142 | 197 |  |  |  |  | - | 307 | - |  |  |  |  | 273 | 274 | 376 |  |  |  |  | 340 | 343 | 474
2024-04-10 | 466 | 162 | 370 | 5.96 | 6.14 | 6.15 |  |  |  | 599 | 605 | 515 |  |  |  |  | 595 | 585 | 464 |  |  |  |  | 521 | 521 | 405 |  |  |  |  | 394 | - | - |  |  |  |  | 193 | 192 | 153 |  |  |  |  | - | - | - |  |  |  |  | 373 | 399 | 304 |  |  |  |  | 460 | 464 | 378
2024-04-11 | 371 | 393 | 400 | 6.08 | 6.01 | 6.1 |  |  |  | 491 | 509 | - |  |  |  |  | 491 | 603 | 522 |  |  |  |  | 415 | 414 | 420 |  |  |  |  | 372 | 364 | 360 |  |  |  |  | 159 | 165 | 167 |  |  |  |  | - | - | - |  |  |  |  | 310 | 318 | 314 |  |  |  |  | 382 | 388 | 394
2024-04-12 | 388 | 582 | 470 | 6.27 | 6.46 | 6.26 |  |  |  | 503 | 522 | 534 |  |  |  |  | 493 | - | 523 |  |  |  |  | 417 | 436 | 454 |  |  |  |  | 346 | 369 | 372 |  |  |  |  | 166 | - | - |  |  |  |  | - | - | - |  |  |  |  | 321 | - | - |  |  |  |  | 393 | - | 456
2024-04-13 | 423 | 450 | 408 | 5.98 | 6.11 | 6.10 |  |  |  | 602 | - | - |  |  |  |  | 544 | - | 550 |  |  |  |  | 440 | 432 | 446 |  |  |  |  | 364 | 365 | 374 |  |  |  |  | - | - | - |  |  |  |  | 362 | 336 | 333 |  |  |  |  | 439 | 360 | 364 |  |  |  |  | - | 433 | 420
2024-04-14 | 376 | 368 | 390 | 6.29 | 5.96 | 6.1 |  |  |  | - | 532 | 550 |  |  |  |  | 494 | 465 | 430 |  |  |  |  | 403 | 395 | 415 |  |  |  |  | - | - | - |  |  |  |  | - | 174 | 165 |  |  |  |  | 306 | 287 | 295 |  |  |  |  | 324 | 321 | 310 |  |  |  |  | 373 | 365 | 380
2024-04-15 | 357 | 356 | 384 | 6.22 | 6.24 | 6.3 |  |  |  | 445 | 499 | 513 |  |  |  |  | 465 | 448 | - |  |  |  |  | 402 | 388 | 387 |  |  |  |  | - | - | - |  |  |  |  | 174 | 167 | - |  |  |  |  | 281 | 270 | 270 |  |  |  |  | 319 | 312 | 316 |  |  |  |  | 360 | 351 | 355 |  |  |  |  | 202.92 | <1 | 8 | <1 | <0,005 | <0,005 | 0 | 1.18 | <0,005 | 139.6 | 125.16 | 12.14 | <0,05 | <0,02 | 1.026 | <0,005 | <0,005 | <0,005 | <0,005 | <0,05
2024-04-16 | 367 | 340 | 348 | 6.19 | 6.22 | 6.24 |  |  |  | 506 | 490 | 479 |  |  |  |  | 456 | 449 | 449 |  |  |  |  | 376 | 381 | 380 |  |  |  |  | - | - | - |  |  |  |  | - | 190 | 174 |  |  |  |  | 275 | 297 | 265 |  |  |  |  | 306 | 310 | 310 |  |  |  |  | 341 | 349 | 350 |  |  |  |  | 193.8 | <1 | 670 | <1 | <0,005 | <0,005 | 0 | 1.24 | <0,005 | 138.36 | 121.98 | 11.36 | <0,05 | <0,02 | 1.6 | <0,005 | <0,005 | <0,005 | <0,005 | <0,05
2024-04-17 | 364 | 323 | 391 | 6.11 | 6.04 | 6.05 |  |  |  | 533 | 435 | 473 |  |  |  |  | - | - | 614 |  |  |  |  | 402 | 344 | 379 |  |  |  |  | - | 342 | 351 |  |  |  |  | - | - | - |  |  |  |  | - | 241 | 261 |  |  |  |  | 312 | 282 | 304 |  |  |  |  | 348 | 317 | 342 |  |  |  |  | 184.11 | <1 | 980 | <1 | <0,005 | <0,005 | 0 | 1.2 | <0,005 | 136.8 | 128.89 | 12.15 | <0,05 | <0,02 | 1.23 | <0,005 | <0,005 | <0,005 | <0,005 | <0,05
2024-04-18 | 405 | 385 | 350 | 6.01 | 6.05 | 6.2 |  |  |  | 500 | 520 | - |  |  |  |  | - | 492 | 486 |  |  |  |  | 396 | 395 | 425 |  |  |  |  | 365 | 360 | 335 |  |  |  |  | - | - | - |  |  |  |  | 277 | 276 | 257 |  |  |  |  | 322 | 323 | 306 |  |  |  |  | 362 | 364 | 344 |  |  |  |  | 219.45 | <1 | 610 | <1 | <0,005 | <0,005 | 0 | 1.18 | <0,005 | 132.9 | 127.18 | 10.78 | <0,05 | <0,02 | 1.342 | <0,005 | <0,005 | <0,005 | <0,005 | <0,05
2024-04-19 | 430 | 361 | 330 | 5.83 | 6.2 | 6.08 |  |  |  | - | - | - |  |  |  |  | - | 469 | - |  |  |  |  | 375 | 465 | 400 |  |  |  |  | 329 | 334 | 317 |  |  |  |  | - | - | 200 |  |  |  |  | 259 | 263 | 250 |  |  |  |  | 305 | 310 | 303 |  |  |  |  | 342 | 348 | 334 |  |  |  |  | 205.77 | <1 | 370 | <1 | <0,005 | <0,005 | 0 | 1.24 | <0,005 | 129.8 | 125.28 | 11.58 | <0,05 | <0,02 | 1.016 | <0,005 | <0,005 | <0,005 | <0,005 | <0,05
2024-04-20 | 329 | 314 | 302 | 6.2 | 6.26 | 6.32 |  |  |  | - | - | - |  |  |  |  | 483 | - | - |  |  |  |  | 386 | 371 | 368 |  |  |  |  | 308 | 302 | 296 |  |  |  |  | 179 | 165 | - |  |  |  |  | 242 | 240 | 237 |  |  |  |  | 293 | 290 | 282 |  |  |  |  | 325 | 327 | 319 |  |  |  |  | 178.98 | <1 | 200 | <1 | <0,005 | <0,005 | 0 | 1.22 | <0,005 | 137.1 | 131.19 | 10.82 | <0,05 | <0,02 | 1.286 | <0,005 | <0,005 | <0,005 | <0,005 | <0,05
2024-04-21 | 321 | 311 | 580 | 6.05 | 6.18 | 6.29 |  |  |  | - | - | - |  |  |  |  | 545 | - | 471 |  |  |  |  | 365 | 371 | 386 |  |  |  |  | 298 | 298 | 307 |  |  |  |  | 167 | 189 | 164 |  |  |  |  | 237 | 267 | 256 |  |  |  |  | 280 | 351 | 290 |  |  |  |  | 318 | 329 | 325 |  |  |  |  | 182.97 | <1 | 160 | 130 | <0,005 | <0,005 | 0 | 1.24 | <0,005 | 140.12 | 124.36 | 11.43 | <0,05 | <0,02 | 1.06 | <0,005 | <0,005 | <0,005 | <0,005 | <0,05
2024-04-22 | 297 | 382 | 300 | 6.09 | 6.18 | 6.02 |  |  |  | - | 561 | 498 |  |  |  |  | - | - | - |  |  |  |  | 379 | - | - |  |  |  |  | - | - | 323 |  |  |  |  | 153 | - | 163 |  |  |  |  | 216 | 242 | 238 |  |  |  |  | 255 | 280 | 282 |  |  |  |  | 297 | 314 | 317 |  |  |  |  | 169.29 | <1 | 220 | 180 | <0,005 | <0,005 | 0 | 1.22 | <0,005 | 136.9 | 158.65 | 11.52 | <0,05 | <0,02 | 1.115 | <0,005 | <0,005 | <0,005 | <0,005 | <0,05
2024-04-23 | 338 | 355 | 403 | 6.04 | 6.75 | 6.22 |  |  |  | 450 | 401 | 445 |  |  |  |  | - | 434 | - |  |  |  |  | - | - | - |  |  |  |  | - | - | 309 |  |  |  |  | - | 271 | 161 |  |  |  |  | 226 | - | 240 |  |  |  |  | 269 | 256 | 271 |  |  |  |  | 303 | 287 | 306 |  |  |  |  | 192.66 | <1 | 130 | <1 | <0,005 | <0,005 | 0 | 1.19 | <0,005 | 143.2 | 126.98 | 10.42 | <0,05 | <0,02 | 1.185 | <0,005 | <0,005 | <0,005 | <0,005 | <0,05
2024-04-24 | 326 | 299 | 324 | 6.27 | 6.23 | 6.14 |  |  |  | - | - | 472 |  |  |  |  | - | 401 | 436 |  |  |  |  | - | - | 173 |  |  |  |  | 284 | 289 | 314 |  |  |  |  | 160 | 156 | 163 |  |  |  |  | 229 | 233 | 251 |  |  |  |  | 260 | 270 | 293 |  |  |  |  | 273 | 304 | 331 |  |  |  |  | 185.82 | <1 | 20 | <1 | <0,005 | <0,005 | 0 | 1.24 | <0,005 | 140 | 132.98 | 10.43 | <0,05 | <0,02 | 1.316 | <0,005 | <0,005 | <0,005 | <0,005 | <0,05
2024-04-25 | 319 | 347 | 344 | 6.05 | 6.09 | 6.35 |  |  |  | - | - | 485 |  |  |  |  | 466 | 445 | 413 |  |  |  |  | 173 | 403 | 395 |  |  |  |  | 287 | 290 | 297 |  |  |  |  | - | - | - |  |  |  |  | 236 | 240 | 239 |  |  |  |  | 311 | 285 | 282 |  |  |  |  | 308 | 337 | 318 |  |  |  |  | - | <1 | 6 | <1 | <0,005 | <0,005 | 0 | 1.22 | <0,005 | 135.8 | 126.31 | 10.81 | <0,05 | <0,02 | 1.304 | <0,005 | <0,005 | <0,005 | <0,005 | <0,05
2024-04-26 | 467 | 362 | 358 | 5.98 | 6.08 | 6.2 |  |  |  | - | 491 | - |  |  |  |  | 449 | 435 | 431 |  |  |  |  | 421 | 409 | 399 |  |  |  |  | 319 | 313 | 304 |  |  |  |  | - | - | - |  |  |  |  | 259 | 252 | 247 |  |  |  |  | 305 | 300 | 294 |  |  |  |  | 343 | 335 | 370 |  |  |  |  | - | <1 | 130 | <1 | <0,005 | <0,005 | 0 | 1.18 | <0,005 | 137.12 | 131.2 | 10.59 | <0,05 | <0,02 | 1.281 | <0,005 | <0,005 | <0,005 | <0,005 | <0,05
2024-04-27 | 348 | 297 | - | 6.07 | 6.3 | - |  |  |  | - | - | - |  |  |  |  | - | - | - |  |  |  |  | 367 | 355 | - |  |  |  |  | 279 | 269 | - |  |  |  |  | - | - | - |  |  |  |  | - | - | - |  |  |  |  | 270 | 264 | - |  |  |  |  | 305 | 284 | - |  |  |  |  | - | <1 | 130 | <1 | <0,005 | <0,005 | 0 | 1.22 | <0,005 | 136.23 | 127.12 | 11.18 | <0,05 | <0,02 | 1.115 | <0,005 | <0,005 | <0,005 | <0,005 | <0,05
2024-04-28 | 406 | 534 | - | 6.09 | 6.41 | - |  |  |  | 524 | 572 | - |  |  |  |  | 603 | 643 | - |  |  |  |  | - | 464 | - |  |  |  |  | - | 364 | - |  |  |  |  | - | - | - |  |  |  |  | 252 | 273 | - |  |  |  |  | 277 | 293 | - |  |  |  |  | - | - | - |  |  |  |  | - | <1 | 50 | <1 | <0,005 | <0,005 | 0 | 1.16 | <0,005 | 128.6 | 125.1 | 9.19 | <0,05 | <0,02 | 1.288 | <0,005 | <0,005 | <0,005 | <0,005 | <0,05
2024-04-29 | 369 |  |  | 6.07 | 6.43 | 6.37 |  | 160.8 | 164.3 | - | - | - |  |  | - | - | 607 | 600 | - | - | 6.48 | - | 258.2 | 422 | 419 | 412 |  | 6.33 |  | 265.5 | - | - | - |  |  |  |  | - | - | - |  |  |  |  | 273 | 264 | 262 |  | 6.31 |  | 265.3 | 299 | 326 | 304 |  | 6.41 |  | 261.5 | 372 | 372 | 374 |  | 6.39 |  | 262 | - | <1 | 28 | <1 | <0,005 | <0,005 | 0 | 1.2 | <0,005 | 132.8 | 131.3 | 10.17 | <0,05 | <0,02 | 1.253 | <0,005 | <0,005 | <0,005 | <0,005 | <0,05
2024-04-30 | 327 |  |  | 6.19 | 6.34 | 7 | 175.2 | 259.3 | 237 | - | 559 | 538 | - | 6.44 |  | 269.3 | - | - | - | - | - | - | - | 383 | 401 | 405 | 6.27 | 6.31 | 178.9 | 168.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 294 | 308 | 312 | 6.28 | 6.33 | 179.9 | 267.3 | 340 | 371 | 371 | 6.41 | 6.31 | 181.5 | 268.5 | - | <1 | 76 | <1 | <0,005 | <0,005 | 0 | 1.25 | <0,005 | 135.3 | 126 | 10.22 | <0,05 | <0,02 | 1.324 | <0,005 | <0,005 | <0,005 | <0,005 | <0,05
2024-05-01 | 347 |  |  | 6.48 | 6.2 | 6.58 | 189 | 275.1 | 256.4 | 559 | 493 | - | 6.61 | 5.81 | 195.3 | 293.9 | 503 | - | 750 | 6.51 | - | 190.4 | - | 380 | 380 | 396 | 6.49 | 5.89 | 189.8 | 290 | - | - | 382 | - | - | - | - | - | - | - | - | - | - | - | 258 | 257 | 262 | 6.54 | 6.76 | 191.9 | 276.7 | 286 | 292 | 301 | 6.48 | 6.33 | 189.2 | 268.5 | - | - | - | - | - | - | - | - | <1 | 62 | <1 | <0,005 | <0,005 | 0 | 1.19 | <0,005 | 132.3 | 127.18 | 10.15 | <0,05 | <0,02 | 1.262 | <0,005 | <0,005 | <0,005 | <0,005 | <0,05
2024-05-02 | 414 |  |  | 6.02 | 6.36 | 6.36 | 175.9 | 172.1 | 172.2 | - | - | - | - | - | - | - | 590 | - | - | 6.42 | - | 181.3 | - | 374 | 374 | 481 | 6.31 | 6.46 | 189.3 | 188.3 | - | 335 | 380 | - | 6.28 | - | 184.1 | - | - | - | - | - | - | - | 252 | 250 | 288 | 6.42 | 6.46 | 185.1 | 187.8 | 302 | 295 | 340 | 6.59 | 6.56 | 187.5 | 181.7 | 350 | 376 | 429 | 6.48 | 6.33 | 176.4 | 187.5 | - | <1 | 30 | <1 | <0,005 | <0,005 | 0 | 1.21 | <0,005 | 134.2 | 127.3 | 10.62 | <0,05 | <0,02 | 1.337 | <0,005 | <0,005 | <0,005 | <0,005 | <0,05
2024-05-03 | 434 |  |  | 6.03 | 6.55 | 6.3 | 265.1 | 261.2 | 265 | - | - | - | - | - | - | - | 651 | - | - | 6.27 | - | 271.4 | - | 410 | 414 | 464 | 6.48 | 6.63 | 272.3 | 253.7 | - | 406 | 381 | - | 6.67 | - | 248.2 | - | - | - | - | - | - | - | 273 | 282 | 281 | 6.51 | 6.65 | 259.4 | 249.2 | 396 | 413 | 414 | 6.54 | 6.63 | 266.2 | 254.9 | 396 | 413 | 414 | 6.43 | 6.33 | 271.8 | 242.5 | -
2024-05-04 | 367 |  |  | 6.48 | 6.31 | 6.19 | 259.1 | 266.4 | 272.5 | - | - | - | - | - | - | - | - | - | 734 | - | - | - | - | 414 | 419 | 445 | 6.26 | 6.3 | 269.5 | 271.9 | 369 | 368 | - | 6.29 | 6.32 | 267.7 | 269.7 | - | - | - | - | - | - | - | 369 | 362 | - | 6.36 | 6.34 | 264.3 | 261.9 | 337 | 342 | 360 | 6.46 | 6.47 | 258 | 260.4 | 409 | 416 | 443 | 6.57 | 6.49 | 254.4 | 258.1 | -
2024-05-05 | 430 |  |  | 6.49 | 6.25 | 6.41 | 252.2 | 269.7 | 262.1 | - | - | 613 | - | - | - | - | 374 | 586 | 580 | 6.17 | 6.32 | 273.2 | 268.5 | 413 | 426 | 434 | 6.29 | 6.4 | 267.7 | 263.5 | - | 410 | 404 | - | 6.36 | - | 265.2 | - | - | - | - | - | - | - | 284 | 287 | 289 | 6.5 | 6.31 | 257.4 | 267.4 | 350 | 347 | 352 | 6.57 | 6.43 | 251.6 | 261.6 | 467 | 417 | 422 | 6.38 | 6.42 | 263.1 | 261.7 | -
2024-05-06 | 408 |  |  | 6.21 |  |  | 267.9 |  |  | 547 |  |  | 6.45 |  | 258 |  | 535 |  |  | 6.37 |  | 261.4 |  | 398 |  |  | 6.35 |  | 262 |  | 366 |  |  | 6.4 |  | 260.1 |  | - |  |  | - |  | - |  | 267 |  |  | 6.23 |  | 268.1 |  | 324 |  |  | 6.36 |  | 260.3 |  | 389 |  |  | 6.39 |  | 260.5 |  | -
2024-05-07 | [65 empty] | -
2024-05-08 | [65 empty] | -
2024-05-09 | [65 empty] | -
2024-05-10 | [65 empty] | -
2024-05-11 | [65 empty] | -
2024-05-12 | [65 empty] | -
2024-05-13 | [65 empty] | -
2024-05-14 | [65 empty] | -
2024-05-15 | [65 empty] | -
Nbr analysis | 92 |  |  | 106 |  |  | 21 |  |  | 46 |  |  | 4 |  | 4 |  | 74 |  |  | 7 |  | 7 |  | 93 |  |  | 14 |  | 14 |  | 72 |  |  | 6 |  | 6 |  | 47 |  |  | 0 |  | 0 |  | 76 |  |  | 12 |  | 12 |  | 102 |  |  | 14 |  | 14 |  | 96 |  |  | 12 |  | 12 |  | 10 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
ph | 175
orp | 90

## CONCENTRAT
Laboratoire de la station de dessalement Jorf Lasfar
CONCENTRAT
Objet: Prestation d’analyse de laboratoire de la station de dessalement d’eau de mer à jorf lasfar
| Cond. (mS/cm) à 25° C | PO43- (mg/l) | T (°C) | Turb (NTU) | Ca2+ (mg/l) | CO32- (mg/l) | HCO3- (mg/l) | SiO2 (mg/l) | TDS (mg/l) | Cl- (mg/l) | Fe2+ (mg/l) | Fe3+ (mg/l) | Bore (mg/l) | NO3- (mg/l) | Al 3+ (mg/l) | Na (g/l) | Mg2+ (mg/l)
2025-04-18 | 93800 | 0.4415 | 20.7 | 0.28 | 1053.8 | 0 | 248.37 | 1.2354 | 59700 | 36871.12 | <0,05 | <0,05 | 6.318 | <0,05 | 0.073 | 14888 | 2636.7

## JTC
Laboratoire de la station de dessalement Jorf Lasfar
CONDUITE DE DISTRIBUTION JORF VERS CASABLANCA
Objet : Prestation d’analyse de laboratoire de la station de dessalement d’eau de mer à jorf lasfar
| Cond. (µS/cm) à 25° C | pH |  |  | orp (mv) |  |  | Turb (NTU) | Cl2 libre (mg/l) | THt(°F) | THt(mg/L)
| P1 | P1 | P2 | P3 | P1 | P2 | P3 | P1 | P1 | P1 | P1
2024-04-01 | 286 | 6.39 | [5 empty] | 1.04 | 0
2024-04-02 | 319 | 6.96 | [5 empty] | 0.71 | 0
2024-04-03 | 387 | 6.02 | [5 empty] | 0.93 | 0
2024-04-04 | 304 | 6.21 | [5 empty] | 0.78 | 0 | 1 | 0.8016
2024-04-05 | 293 | 6.29 | [5 empty] | 0.65 | 0 | 0.8 | 0.8016
2024-04-06 | 270 | 6.24 | [5 empty] | 0.6 | 0 | 0.6 | 0.7801
2024-04-07 | 274 | 6.18 | [5 empty] | 0.8 | 0 | 0.9 | 0.801
2024-04-08 | 261 | 6.23 | [5 empty] | 0.95 | 0 | 0.5 | 0.4008
2024-04-09 | 250 | 6.15 | [5 empty] | 4.25 | 0 | 0.8 | 0.7601
2024-04-10 | 371 | 6.15 | [5 empty] | 5.78 | 0.07 | 1.1 | 0.9619
2024-04-11 | 308 | 6.26 | [5 empty] | 0.49 | 0 | 0.9 | 0.8016
2024-04-12 | 353 | 6.21 | [5 empty] | 0.48 | 0 | 0.85 | 0.76
2024-04-13 | 391 | 6.23 | [5 empty] | 0.21 | 0 | 1 | 0.4008
2024-04-14 | 399 | 6.32 | [5 empty] | 0.46 | 0 | 0.8 | 0.8017
2024-04-15 | 316 | 6.3 | [5 empty] | 0.59 | 0 | 1.04 | 0.4016
2024-04-16 | 303 | 6.25 | [5 empty] | 0.62 | 0 | 0.7 | 0.4008
2024-04-17 | 298 | 6.27 | [5 empty] | 0.48 | 0 | 0.8 | 0.4006
2024-04-18 | 346 | 6.09 | [5 empty] | 0.3 | 0 | 1 | 0.8016
2024-04-19 | 285 | 5.96 | [5 empty] | 0.2 | 0 | 0.8 | 1.002
2024-04-20 | 281 | 6.27 | [5 empty] | 0.25 | 0 | 0.9 | 0.641
2024-04-21 | 280 | 6.21 | [5 empty] | 0.2 | 0 | 0.9 | 0.8016
2024-04-22 | 261 | 6.28 | [5 empty] | 0.25 | 0 | 1 | 0.4008
2024-04-23 | 371 | 6.3 | [5 empty] | 0.25 | 0 | 1 | 0.48096
2024-04-24 | 292 | 6.25 | [5 empty] | 0.33 | 0 | 0.8 | 0.401
2024-04-25 | 287 | 6.3 | [5 empty] | 0.27 | 0 | 0.95 | 0.7215
2024-04-26 | 303 | 6.1 | [5 empty] | 0.32 | 0 | 0.9 | 0.816
2024-04-27 | 260 | 6.21 | [5 empty] | 0.39 | 0 | 0.7 | 0.6413
2024-04-28 | 280 | 6.26 | [5 empty] | 0.21 | 0 | 1 | 0.4008
2024-04-29 | 278 | 6.23 | 6.78 | 6.2 |  | 244 | 246 | 0.2 | 0 | 1.1 | 0.4008
2024-04-30 | 310 | 6.46 | 6.42 | 7.16 | 189 | 264.9 | 227.9 | 0.39 | 0 | 1.5 | 1.203
2024-05-01 | 356 | 6.89 | 6.19 | 6.85 | 208.9 | 275.3 | 243.6 | 0.24 | 0 | 1.6 | 2.004
2024-05-02 | 316 | 6.75 | 6.61 | 6.41 | 200.1 | 199.7 | 265.6 | 0.29 | 0 | 0.8 | 0.4008
2024-05-03 | 308 | 6.5 | 6.08 | 6.12 | 256.1 | 277.4 | 275.1 | 0.32 | 0 | 1.1 | 0.4008
2024-05-04 | 285 | 6.29 | 6.31 | 6.39 | 270.4 | 266.8 | 263.4 | 0.19 | 0 | 1 | 0.4008
2024-05-05 | 432 | 6.44 | 6.33 | 6.48 | 260.8 | 266.1 | 258.8 | 0.28 | 0 | 0.9 | 0.3706
2024-05-06 | 314 | 6.33 |  |  | 263.7 |  |  | 0.18 | 0 | 0.8 | 0.4008
2024-05-07
2024-05-08
2024-05-09
2024-05-10
2024-05-11
2024-05-12
2024-05-13
2024-05-14
2024-05-15
Nbr analysis | 36 | 50 |  |  | 21 |  |  | 36 | 36 | 33 | 33

## J2C
Laboratoire de la station de dessalement Jorf Lasfar
CONDUITE DE DISTRIBUTION JORF VERS CASABLANCA
Objet : Prestation d’analyse de laboratoire de la station de dessalement d’eau de mer à jorf lasfar
| CONDUITE SRM |  | BASSIN |  | JTC
DATE | HEURE | Cl2 libre (mg/l) | HEURE | Cl2 libre (mg/l) | HEURE | Cl2 libre (mg/l)
2025-05-04 |  |  |  |  | 16h37 | 0
2025-05-05 |  |  | 17h30 | 0.19
2025-05-06 | 23h37 | 0.06 | 00h00 | 0.06
| 00h00 | 0 | 2h30 | 1.12
| 00h40 | 0.1
| 1h07 | 1.17
| 2h30 | 1.07

## Nbr analysis totale
Item | 1.5 mois | Qte rèalise
Temperature | 418.5 | 311
pH | 837 | 558
Conductivity | 1348.5 | 1258
Chlore libre Cl2 | 558 | 449
ORP RED /OX | 697.5 | 444
Turbidity | 418.5 | 372
Silt density index (SDI) | 186 | 164
Total Suspended Solids (TSS) | 46.5 | 36
Microbiology (fecal coli, total coli,Escherichia coli) | 186 | 162
Iron (Fe3+ / Fe2+) | 186 | 108
TOC | 46.5 | 36
Chlorophyll | 93 | 36
ATP | 93 | 36
Oil & Grease | 46.5 | 36
Manganese | 46.5 | 36
Sodium | 46.5 | 36
Magnesium | 46.5 | 51
Calcium | 46.5 | 51
Chloride | 46.5 | 36
Sulfate | 46.5 | 36
Nitrate | 46.5 | 36
Boron | 93 | 36
Total Dissolved Solids (TDS) | 46.5 | 46
Aluminum (Al) | 93 | 36
Phosphorus (PO4) | 46.5 | 36
Silica | 46.5 | 18
Carbonate | 46.5 | 36
Bicarbonate | 46.5 | 36
CO2 | 46.5 | 18
Nitrite | 46.5 | 18
Arsenic | 46.5 | 18
Plomb | 46.5 | 18
Cadmium | 46.5 | 18
Copper | 46.5 | 18
Total HT